## Sheet1
type | id | description | category | requires | arguments | taskId | name | periodicity
Task | urn:ngsi-ld:Task:Assessment:A28-S2-G-F-V05:SpecElUse-1 | {'type': 'Property', 'value': 'Assessments: Determines if any faults are present in the given system'} | {'type': 'Property', 'value': 'Assessment'} | {'type': 'Property', 'value': {'ElecUse': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Total-Load', 'unit': 'KWH'}, 'ExtFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Exhaust-Fan-Flow', 'unit': 'MQH'}, 'ExtTemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-External', 'unit': 'CEL'}, 'SupFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Flow', 'unit': 'MQH'}}} | {'type': 'Property', 'value': {'FD_ID': 'SpecificElectricityUseHistorical', 'HDBscan_grid_max_points': [1000, 5000, 10000, 50000, 100000, 500000], 'HDBscan_grid_min_cluster_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'HDBscan_min_points': [500, 1000, 2000, 3000, 4000], 'HDBscan_update': [24, 48, 72, 96, 120, 144, 168, 336], 'IQR_maximum_points': [100, 200, 300, 400, 500, 600, 700, 800, 900, 1000], 'IQR_minimum_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'IQR_multiplier': 1.5, 'data_time_resolution': [5, 15, 30, 60], 'historical_max_time': [30, 60, 90, 120, 150, 180]}} | {'type': 'Property', 'value': 'A28-S2-G-F-V05'} | {'type': 'Property', 'value': 'AHU Fault detection'}
Task | urn:ngsi-ld:Task:Assessment:A28-S2-G-F-V05:SpecElUse-2 | {'type': 'Property', 'value': 'Assessments: Determines if any faults are present in the given system'} | {'type': 'Property', 'value': 'Assessment'} | {'type': 'Property', 'value': {'ElecUse': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Total-Load', 'unit': 'KWH'}, 'ExtFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Exhaust-Fan-Flow', 'unit': 'MQH'}, 'ExtFanSignal': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setvalue-Exhaust-Fan-Control-Signal', 'unit': 'P1'}, 'SupFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Flow', 'unit': 'MQH'}, 'SupFanSignal': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setpoint-Supply-Fan-Control', 'unit': 'P1'}}} | {'type': 'Property', 'value': {'FD_ID': 'SpecificElectricityUseHistorical1', 'HDBscan_grid_max_points': [1000, 5000, 10000, 50000, 100000, 500000], 'HDBscan_grid_min_cluster_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'HDBscan_min_points': [500, 1000, 2000, 3000, 4000], 'HDBscan_update': [24, 48, 72, 96, 120, 144, 168, 336], 'IQR_maximum_points': [100, 200, 300, 400, 500, 600, 700, 800, 900, 1000], 'IQR_minimum_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'IQR_multiplier': 1.5, 'data_time_resolution': [5, 15, 30, 60], 'historical_max_time': [30, 60, 90, 120, 150, 180]}} | {'type': 'Property', 'value': 'A28-S2-G-F-V05'} | {'type': 'Property', 'value': 'AHU Fault detection'}
Task | urn:ngsi-ld:Task:Assessment:A28-S2-G-F-V05:SpecFanPower-1 | {'type': 'Property', 'value': 'Assessments: Determines if any faults are present in the given system'} | {'type': 'Property', 'value': 'Assessment'} | {'type': 'Property', 'value': {'ExtFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Exhaust-Fan-Flow', 'unit': 'MQH'}, 'ExtFanPower': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Exhaust-Fan-Power', 'unit': 'KWT'}, 'ExtFanSignal': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setvalue-Exhaust-Fan-Control-Signal', 'unit': 'P1'}, 'SupFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Flow', 'unit': 'MQH'}, 'SupFanPower': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Power', 'unit': 'KWT'}, 'SupFanSignal': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setpoint-Supply-Fan-Control', 'unit': 'P1'}}} | {'type': 'Property', 'value': {'FD_ID': 'SpecificFanPower1', 'HDBscan_grid_max_points': [1000, 5000, 10000, 50000, 100000, 500000], 'HDBscan_grid_min_cluster_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'HDBscan_min_points': [500, 1000, 2000, 3000, 4000], 'HDBscan_update': [24, 48, 72, 96, 120, 144, 168, 336], 'IQR_maximum_points': [100, 200, 300, 400, 500, 600, 700, 800, 900, 1000], 'IQR_minimum_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'IQR_multiplier': 1.5, 'data_time_resolution': [5, 15, 30, 60], 'historical_max_time': [30, 60, 90, 120, 150, 180]}} | {'type': 'Property', 'value': 'A28-S2-G-F-V05'} | {'type': 'Property', 'value': 'AHU Fault detection'}
Task | urn:ngsi-ld:Task:Assessment:A28-S2-G-F-V05:SpecFanPower-2 | {'type': 'Property', 'value': 'Assessments: Determines if any faults are present in the given system'} | {'type': 'Property', 'value': 'Assessment'} | {'type': 'Property', 'value': {'ExtFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Exhaust-Fan-Flow', 'unit': 'MQH'}, 'ExtFanPower': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Exhaust-Fan-Power', 'unit': 'KWT'}, 'ExtFanSignal': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setvalue-Exhaust-Fan-Control-Signal', 'unit': 'P1'}, 'SupFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Flow', 'unit': 'MQH'}, 'SupFanPower': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Power', 'unit': 'KWT'}, 'SupFanSignal': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setpoint-Supply-Fan-Control', 'unit': 'P1'}}} | {'type': 'Property', 'value': {'FD_ID': 'SpecificFanPower1', 'HDBscan_grid_max_points': [1000, 5000, 10000, 50000, 100000, 500000], 'HDBscan_grid_min_cluster_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'HDBscan_min_points': [500, 1000, 2000, 3000, 4000], 'HDBscan_update': [24, 48, 72, 96, 120, 144, 168, 336], 'IQR_maximum_points': [100, 200, 300, 400, 500, 600, 700, 800, 900, 1000], 'IQR_minimum_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'IQR_multiplier': 1.5, 'data_time_resolution': [5, 15, 30, 60], 'historical_max_time': [30, 60, 90, 120, 150, 180]}} | {'type': 'Property', 'value': 'A28-S2-G-F-V05'} | {'type': 'Property', 'value': 'AHU Fault detection'}
Task | urn:ngsi-ld:Task:Assessment:A28-S2-G-F-V05:SpecHeatUse-1 | {'type': 'Property', 'value': 'Assessments: Determines if any faults are present in the given system'} | {'type': 'Property', 'value': 'Assessment'} | {'type': 'Property', 'value': {'AfterHETemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-HE', 'unit': 'CEL'}, 'ExtFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Exhaust-Fan-Flow', 'unit': 'MQH'}, 'ExtractionAirTemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-Extraction', 'unit': 'CEL'}, 'HeatEnergyUse': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Energy-Consumed-Heating-Coil', 'unit': 'WHR'}, 'IntakeAirTemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-Intake', 'unit': 'CEL'}, 'SupFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Flow', 'unit': 'MQH'}}} | {'type': 'Property', 'value': {'FD_ID': 'SpecificHeatingEnergyUseHistorical1', 'HDBscan_grid_max_points': [1000, 5000, 10000, 50000, 100000, 500000], 'HDBscan_grid_min_cluster_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'HDBscan_min_points': [500, 1000, 2000, 3000, 4000], 'HDBscan_update': [24, 48, 72, 96, 120, 144, 168, 336], 'IQR_maximum_points': [100, 200, 300, 400, 500, 600, 700, 800, 900, 1000], 'IQR_minimum_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'IQR_multiplier': 1.5, 'data_time_resolution': [5, 15, 30, 60], 'historical_max_time': [30, 60, 90, 120, 150, 180]}} | {'type': 'Property', 'value': 'A28-S2-G-F-V05'} | {'type': 'Property', 'value': 'AHU Fault detection'}
Task | urn:ngsi-ld:Task:Assessment:A28-S2-G-F-V05:SpecHeatUse-2 | {'type': 'Property', 'value': 'Assessments: Determines if any faults are present in the given system'} | {'type': 'Property', 'value': 'Assessment'} | {'type': 'Property', 'value': {'ExtTemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-External', 'unit': 'CEL'}, 'HeatEnergyUse': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Energy-Consumed-Heating-Coil', 'unit': 'WHR'}, 'SupFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Flow', 'unit': 'MQH'}}} | {'type': 'Property', 'value': {'FD_ID': 'SpecificHeatingEnergyUseHistorical2', 'HDBscan_grid_max_points': [1000, 5000, 10000, 50000, 100000, 500000], 'HDBscan_grid_min_cluster_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'HDBscan_min_points': [500, 1000, 2000, 3000, 4000], 'HDBscan_update': [24, 48, 72, 96, 120, 144, 168, 336], 'IQR_maximum_points': [100, 200, 300, 400, 500, 600, 700, 800, 900, 1000], 'IQR_minimum_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'IQR_multiplier': 1.5, 'data_time_resolution': [5, 15, 30, 60], 'historical_max_time': [30, 60, 90, 120, 150, 180]}} | {'type': 'Property', 'value': 'A28-S2-G-F-V05'} | {'type': 'Property', 'value': 'AHU Fault detection'}
Task | urn:ngsi-ld:Task:Assessment:A28-S2-G-F-V05:SpecHeatUse-3 | {'type': 'Property', 'value': 'Assessments: Determines if any faults are present in the given system'} | {'type': 'Property', 'value': 'Assessment'} | {'type': 'Property', 'value': {'AfterHETemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-HE', 'unit': 'CEL'}, 'HeatEnergyUse': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Energy-Consumed-Heating-Coil', 'unit': 'WHR'}, 'SupAirTemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-Air-Supply', 'unit': 'CEL'}, 'SupFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Flow', 'unit': 'MQH'}}} | {'type': 'Property', 'value': {'FD_ID': 'SpecificHeatingEnergyUseHistorical', 'HDBscan_grid_max_points': [1000, 5000, 10000, 50000, 100000, 500000], 'HDBscan_grid_min_cluster_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'HDBscan_min_points': [500, 1000, 2000, 3000, 4000], 'HDBscan_update': [24, 48, 72, 96, 120, 144, 168, 336], 'IQR_maximum_points': [100, 200, 300, 400, 500, 600, 700, 800, 900, 1000], 'IQR_minimum_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'IQR_multiplier': 1.5, 'data_time_resolution': [5, 15, 30, 60], 'historical_max_time': [30, 60, 90, 120, 150, 180]}} | {'type': 'Property', 'value': 'A28-S2-G-F-V05'} | {'type': 'Property', 'value': 'AHU Fault detection'} | {'type': 'Property', 'value': '*/5 * * * *'}
Task | urn:ngsi-ld:Task:Assessment:A28-S2-G-F-V05:SupPresDevAvg-1 | {'type': 'Property', 'value': 'Assessments: Determines if any faults are present in the given system'} | {'type': 'Property', 'value': 'Assessment'} | {'type': 'Property', 'value': {'SupFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Flow', 'unit': 'MQH'}, 'SupFanOnOff': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Supply fan on/off signal', 'unit': 'Boolean'}, 'SupFanSignal': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setpoint-Supply-Fan-Control', 'unit': 'P1'}, 'SupPres': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Air-Pressure-Supply', 'unit': 'PAL'}, 'SupPresSetp': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setpoint-Air-Pressure-Supply', 'unit': 'PAL'}}} | {'type': 'Property', 'value': {'FD_ID': 'SupplyPressureDeviationAverageHistoricalInUse1', 'HDBscan_grid_max_points': [1000, 5000, 10000, 50000, 100000, 500000], 'HDBscan_grid_min_cluster_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'HDBscan_min_points': [500, 1000, 2000, 3000, 4000], 'HDBscan_update': [24, 48, 72, 96, 120, 144, 168, 336], 'IQR_maximum_points': [100, 200, 300, 400, 500, 600, 700, 800, 900, 1000], 'IQR_minimum_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'IQR_multiplier': 1.5, 'data_time_resolution': [5, 15, 30, 60], 'historical_max_time': [30, 60, 90, 120, 150, 180]}} | {'type': 'Property', 'value': 'A28-S2-G-F-V05'} | {'type': 'Property', 'value': 'AHU Fault detection'}
Task | urn:ngsi-ld:Task:Assessment:A28-S2-G-F-V05:SupPresDevAvg-2 | {'type': 'Property', 'value': 'Assessments: Determines if any faults are present in the given system'} | {'type': 'Property', 'value': 'Assessment'} | {'type': 'Property', 'value': {'SupFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Flow', 'unit': 'MQH'}, 'SupFanOnOff': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Supply fan on/off signal', 'unit': 'Boolean'}, 'SupFanSignal': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setpoint-Supply-Fan-Control', 'unit': 'P1'}, 'SupPres': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Air-Pressure-Supply', 'unit': 'PAL'}, 'SupPresSetp': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setpoint-Air-Pressure-Supply', 'unit': 'PAL'}}} | {'type': 'Property', 'value': {'FD_ID': 'SupplyPressureDeviationAverageHistoricalInUse1', 'HDBscan_grid_max_points': [1000, 5000, 10000, 50000, 100000, 500000], 'HDBscan_grid_min_cluster_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'HDBscan_min_points': [500, 1000, 2000, 3000, 4000], 'HDBscan_update': [24, 48, 72, 96, 120, 144, 168, 336], 'IQR_maximum_points': [100, 200, 300, 400, 500, 600, 700, 800, 900, 1000], 'IQR_minimum_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'IQR_multiplier': 1.5, 'data_time_resolution': [5, 15, 30, 60], 'historical_max_time': [30, 60, 90, 120, 150, 180]}} | {'type': 'Property', 'value': 'A28-S2-G-F-V05'} | {'type': 'Property', 'value': 'AHU Fault detection'}
Task | urn:ngsi-ld:Task:Assessment:A28-S2-G-F-V05:SupTempDevAvg-1 | {'type': 'Property', 'value': 'Assessments: Determines if any faults are present in the given system'} | {'type': 'Property', 'value': 'Assessment'} | {'type': 'Property', 'value': {'ExtTemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature', 'unit': 'CEL'}, 'SupFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Flow', 'unit': 'MQH'}, 'SupFanOnOff': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Supply fan on/off signal', 'unit': 'Boolean'}, 'SupTemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-Air-Supply', 'unit': 'CEL'}, 'SupTempSetp': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setpoint-Temperature-Air-Supply', 'unit': 'CEL'}}} | {'type': 'Property', 'value': {'FD_ID': 'SupplyTemperatureDeviationAverageHistorical', 'HDBscan_grid_max_points': [1000, 5000, 10000, 50000, 100000, 500000], 'HDBscan_grid_min_cluster_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'HDBscan_min_points': [500, 1000, 2000, 3000, 4000], 'HDBscan_update': [24, 48, 72, 96, 120, 144, 168, 336], 'IQR_maximum_points': [100, 200, 300, 400, 500, 600, 700, 800, 900, 1000], 'IQR_minimum_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'IQR_multiplier': 1.5, 'data_time_resolution': [5, 15, 30, 60], 'historical_max_time': [30, 60, 90, 120, 150, 180]}} | {'type': 'Property', 'value': 'A28-S2-G-F-V05'} | {'type': 'Property', 'value': 'AHU Fault detection'}
Task | urn:ngsi-ld:Task:Assessment:A28-S2-G-F-V05:SupTempDevAvg-2 | {'type': 'Property', 'value': 'Assessments: Determines if any faults are present in the given system'} | {'type': 'Property', 'value': 'Assessment'} | {'type': 'Property', 'value': {'AfterHETemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-HE', 'unit': 'CEL'}, 'ExtFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Exhaust-Fan-Flow', 'unit': 'MQH'}, 'ExtractionAirTemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-Extraction', 'unit': 'CEL'}, 'IntakeAirTemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-Intake', 'unit': 'CEL'}, 'SupFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Flow', 'unit': 'MQH'}, 'SupFanOnOff': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Supply fan on/off signal', 'unit': 'Boolean'}, 'SupTemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-Air-Supply', 'unit': 'CEL'}, 'SupTempSetp': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setpoint-Temperature-Air-Supply', 'unit': 'CEL'}}} | {'type': 'Property', 'value': {'FD_ID': 'SupplyTemperatureDeviationAverageHistorical1', 'HDBscan_grid_max_points': [1000, 5000, 10000, 50000, 100000, 500000], 'HDBscan_grid_min_cluster_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'HDBscan_min_points': [500, 1000, 2000, 3000, 4000], 'HDBscan_update': [24, 48, 72, 96, 120, 144, 168, 336], 'IQR_maximum_points': [100, 200, 300, 400, 500, 600, 700, 800, 900, 1000], 'IQR_minimum_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'IQR_multiplier': 1.5, 'data_time_resolution': [5, 15, 30, 60], 'historical_max_time': [30, 60, 90, 120, 150, 180]}} | {'type': 'Property', 'value': 'A28-S2-G-F-V05'} | {'type': 'Property', 'value': 'AHU Fault detection'}
Task | urn:ngsi-ld:Task:Assessment:A28-S2-G-F-V05:SupTempDevAvg-3 | {'type': 'Property', 'value': 'Assessments: Determines if any faults are present in the given system'} | {'type': 'Property', 'value': 'Assessment'} | {'type': 'Property', 'value': {'HeatEnergyUse': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Energy-Consumed-Heating-Coil', 'unit': 'WHR'}, 'SupFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Flow', 'unit': 'MQH'}, 'SupFanOnOff': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Supply fan on/off signal', 'unit': 'Boolean'}, 'SupTemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-Air-Supply', 'unit': 'CEL'}, 'SupTempSetp': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setpoint-Temperature-Air-Supply', 'unit': 'CEL'}}} | {'type': 'Property', 'value': {'FD_ID': 'SupplyTemperatureDeviationAverageHistorical2', 'HDBscan_grid_max_points': [1000, 5000, 10000, 50000, 100000, 500000], 'HDBscan_grid_min_cluster_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'HDBscan_min_points': [500, 1000, 2000, 3000, 4000], 'HDBscan_update': [24, 48, 72, 96, 120, 144, 168, 336], 'IQR_maximum_points': [100, 200, 300, 400, 500, 600, 700, 800, 900, 1000], 'IQR_minimum_points': [10, 20, 30, 40, 50, 60, 70, 80, 90, 100], 'IQR_multiplier': 1.5, 'data_time_resolution': [5, 15, 30, 60], 'historical_max_time': [30, 60, 90, 120, 150, 180]}} | {'type': 'Property', 'value': 'A28-S2-G-F-V05'} | {'type': 'Property', 'value': 'AHU Fault detection'}
Task | urn:ngsi-ld:Task:Assessment:A53_Dishwasher-Fault-Detection | {'type': 'Property', 'value': 'Detects anomalies through the energy consumption of dishwasher devices.'} | {'type': 'Property', 'value': 'Assessment'} | {'type': 'Property', 'value': {'energy_sensor': {'type': 'Device', 'category': 'Dishwasher'}, 'target_device': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'ActiveEnergyConsumed'}}} |  | {'type': 'Property', 'value': 'A53'} | {'type': 'Property', 'value': 'Dishwasher Anomaly Detection Task'} | {'type': 'Property', 'value': '@daily'}
Task | urn:ngsi-ld:Task:KPI:Average-Supply-Pressure-Deviation | {'type': 'Property', 'value': 'KPI definition for the average supply pressure deviation in the AHU, takes as input a timeseries of supply pressure and supply pressure setpoints and outputs the average supply pressure deviation over the entire timeseries as a float'} | {'type': 'Property', 'value': 'KPI'} | {'type': 'Property', 'value': {'SupPres': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Air-Pressure-Supply', 'unit': 'PAL'}, 'SupPresSetp': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setpoint-Air-Pressure-Supply', 'unit': 'PAL'}}} | {'type': 'Property', 'value': {'scope': {'type': 'enum', 'values': ['1 minute', '5 minutes', '15 minutes', 'hourly', 'daily', 'weekly', 'yearly']}}} | {'type': 'Property', 'value': 'A28-K:SC000-V01'} | {'type': 'Property', 'value': 'Average Supply Pressure Deviation'}
Task | urn:ngsi-ld:Task:KPI:Average-Supply-Temperature-Deviation | {'type': 'Property', 'value': 'KPI definition for the average supply temperature deviation in the AHU, takes as input a timeseries of supply temperature and supply temperature setpoints and outputs the average supply temperature deviation over the entire timeseries as a float'} | {'type': 'Property', 'value': 'KPI'} | {'type': 'Property', 'value': {'SupTemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-Air-Supply', 'unit': 'CEL'}, 'SupTempSetp': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setpoint-Temperature-Air-Supply', 'unit': 'CEL'}}} | {'type': 'Property', 'value': {'scope': {'type': 'enum', 'values': ['1 minute', '5 minutes', '15 minutes', 'hourly', 'daily', 'weekly', 'yearly']}}} | {'type': 'Property', 'value': 'A28-K:SC000-V03'} | {'type': 'Property', 'value': 'Average Supply Temperature Deviation'}
Task | urn:ngsi-ld:Task:KPI:Cooling-Peak-Power | {'type': 'Property', 'value': 'KPI definition for the cooling peak power in the AHU, takes as input a timeseries of electrical energy use for Cooling device and outputs the electrical peak power over the entire timeseries as a float'} | {'type': 'Property', 'value': 'KPI'} | {'type': 'Property', 'value': {'ElecUse': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Energy-Consumed-Heating-Coil', 'unit': 'WHR'}}} | {'type': 'Property', 'value': {'scope': {'type': 'enum', 'values': ['1 minute', '5 minutes', '15 minutes', 'hourly', 'daily', 'weekly', 'yearly']}}} | {'type': 'Property', 'value': 'A28-K:BP100-V03'} | {'type': 'Property', 'value': 'Cooling Peak Power'}
Task | urn:ngsi-ld:Task:KPI:Electrical-Peak-Power | {'type': 'Property', 'value': 'KPI definition for the electrical peak power in the AHU, takes as input a timeseries of electrical energy use and outputs the electrical peak power over the entire timeseries as a float'} | {'type': 'Property', 'value': 'KPI'} | {'type': 'Property', 'value': {'ElecUse': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Total-Load', 'unit': 'KWT'}}} | {'type': 'Property', 'value': {'scope': {'type': 'enum', 'values': ['1 minute', '5 minutes', '15 minutes', 'hourly', 'daily', 'weekly', 'yearly']}}} | {'type': 'Property', 'value': 'A28-K:BP100-V01'} | {'type': 'Property', 'value': 'Electrical Peak Power'}
Task | urn:ngsi-ld:Task:KPI:Electricity-Use | {'type': 'Property', 'value': 'KPI definition for the electricity use in the AHU, takes as input a timeseries of electricity use and outputs the sum electricity use over the entire timeseries as a float'} | {'type': 'Property', 'value': 'KPI'} | {'type': 'Property', 'value': {'ElecUse': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Accumulated-Load', 'unit': 'KWH'}}} | {'type': 'Property', 'value': {'scope': {'type': 'enum', 'values': ['1 minute', '5 minutes', '15 minutes', 'hourly', 'daily', 'weekly', 'yearly']}}} | {'type': 'Property', 'value': 'A28-K:EP100-V01'} | {'type': 'Property', 'value': 'Electricity Use'}
Task | urn:ngsi-ld:Task:KPI:Electricity_Use | {'type': 'Property', 'value': 'KPI definition for the heating energy use in the AHU, takes as input a timeseries of heating energy use and outputs the sum electricity use over the entire timeseries as a float'} | {'type': 'Property', 'value': 'KPI'} | {'type': 'Property', 'value': {'ElecUse': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Energy-Consumed-Heating-Coil', 'unit': 'WHR'}}} | {'type': 'Property', 'value': {'scope': {'type': 'enum', 'values': ['1 minute', '5 minutes', '15 minutes', 'hourly', 'daily', 'weekly', 'yearly']}}} | {'type': 'Property', 'value': 'A28-K:EP200-V01'} | {'type': 'Property', 'value': 'Heating Energy Use'}
Task | urn:ngsi-ld:Task:KPI:Energy-Use-Intensity | {'type': 'Property', 'value': 'KPI definition for Energy Use Intensity (EUI). Takes as input a timeseries of killowatt/killowatt per hour measurements and the area of the physical space in squared meters and outputs the EUI.'} | {'type': 'Property', 'value': 'KPI'} | {'type': 'Property', 'value': {'SpacialContext': {'type': ['Building', 'Zone', 'Space'], 'area': True}, 'TotalLoad': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': ['Accumulated-Load', 'Total-Load'], 'unit': ['KWH', 'KWT']}}} |  | {'type': 'Property', 'value': 'A01-K:00001-V01'} | {'type': 'Property', 'value': 'Energy Use Intensity'} | {'type': 'Property', 'value': ['@hourly', '@weekly', '@monthly', '@yearly']}
Task | urn:ngsi-ld:Task:KPI:Fan_Electricity_Use | {'type': 'Property', 'value': 'KPI definition for the electricity use for the fan, takes as input a timeseries of electricity use and outputs the sum electricity use over the entire timeseries as a float'} | {'type': 'Property', 'value': 'KPI'} | {'type': 'Property', 'value': {'ElecUse': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Exhaust-Fan-Power', 'unit': 'KWT'}}} | {'type': 'Property', 'value': {'scope': {'type': 'enum', 'values': ['1 minute', '5 minutes', '15 minutes', 'hourly', 'daily', 'weekly', 'yearly']}}} | {'type': 'Property', 'value': 'A28-K:EP100-V02'} | {'type': 'Property', 'value': 'Fan Electricity Use'}
Task | urn:ngsi-ld:Task:KPI:Heat_Exchanger_Efficiency | {'type': 'Property', 'value': 'KPI definition for the heat exchanger efficiency in the rotary heat exchanger, takes as input a timeseries of supply and extraction flow and air temperature and outputs the the deviation between the real and theoratical possiple heat exchanger efficiency over the entire timeseries as a float'} | {'type': 'Property', 'value': 'KPI'} | {'type': 'Property', 'value': {'ExtFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Exhaust-Fan-Flow', 'unit': 'MQH'}, 'ExtTemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-Extraction', 'unit': 'CEL'}, 'SupFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Flow', 'unit': 'MQH'}, 'SupTemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-Air-Supply', 'unit': 'CEL'}, 'SupTempSP': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setpoint-Temperature-Air-Supply', 'unit': 'CEL'}, 'TempAfterHE': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-HE', 'unit': 'CEL'}, 'TempIntake': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-Intake', 'unit': 'CEL'}}} | {'type': 'Property', 'value': {'c_p': 1.006, 'scope': {'type': 'enum', 'values': ['1 minute', '5 minutes', '15 minutes', 'hourly', 'daily', 'weekly', 'yearly']}}} | {'type': 'Property', 'value': 'A28-K:SC130-V01'} | {'type': 'Property', 'value': 'Heat Exchanger Efficiency'}
Task | urn:ngsi-ld:Task:KPI:Heating-Peak-Power | {'type': 'Property', 'value': 'KPI definition for the heating peak power in the AHU, takes as input a timeseries of electrical energy use for heating device and outputs the electrical peak power over the entire timeseries as a float'} | {'type': 'Property', 'value': 'KPI'} | {'type': 'Property', 'value': {'ElecUse': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Energy-Consumed-Heating-Coil', 'unit': 'WHR'}}} | {'type': 'Property', 'value': {'scope': {'type': 'enum', 'values': ['1 minute', '5 minutes', '15 minutes', 'hourly', 'daily', 'weekly', 'yearly']}}} | {'type': 'Property', 'value': 'A28-K:BP100-V02'} | {'type': 'Property', 'value': 'Heating Peak Power'}
Task | urn:ngsi-ld:Task:KPI:Max-Supply-Pressure-Deviation | {'type': 'Property', 'value': 'KPI definition for the maximum supply pressure deviation in the AHU, takes as input a timeseries of supply pressure and supply pressure setpoints and outputs the maximum supply pressure deviation over the entire timeseries as a float'} | {'type': 'Property', 'value': 'KPI'} | {'type': 'Property', 'value': {'SupPres': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Air-Pressure-Supply', 'unit': 'PAL'}, 'SupPresSetp': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setpoint-Air-Pressure-Supply', 'unit': 'PAL'}}} | {'type': 'Property', 'value': {'scope': {'type': 'enum', 'values': ['1 minute', '5 minutes', '15 minutes', 'hourly', 'daily', 'weekly', 'yearly']}}} | {'type': 'Property', 'value': 'A28-K:SC000-V02'} | {'type': 'Property', 'value': 'Max Supply Pressure Deviation'}
Task | urn:ngsi-ld:Task:KPI:Max-Supply-Temperature-Deviation | {'type': 'Property', 'value': 'KPI definition for the max supply temperature deviation in the AHU, takes as input a timeseries of supply temperature and supply temperature setpoints and outputs the max supply temperature deviation over the entire timeseries as a float'} | {'type': 'Property', 'value': 'KPI'} | {'type': 'Property', 'value': {'SupTemp': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Temperature-Air-Supply', 'unit': 'CEL'}, 'SupTempSetp': {'type': 'Device', 'category': 'Actuator', 'controlsProperty': 'Setpoint-Temperature-Air-Supply', 'unit': 'CEL'}}} | {'type': 'Property', 'value': {'scope': {'type': 'enum', 'values': ['1 minute', '5 minutes', '15 minutes', 'hourly', 'daily', 'weekly', 'yearly']}}} | {'type': 'Property', 'value': 'A28-K:SC000-V04'} | {'type': 'Property', 'value': 'Max Supply Temperature Deviation'}
Task | urn:ngsi-ld:Task:KPI:specific_electicity_use | {'type': 'Property', 'value': 'KPI definition for the specific electricity use for the AHU, takes as input a timeseries of supply air flow, extracion air flow, and electricity use and outputs the specific electricity use over the entire timeseries as a float'} | {'type': 'Property', 'value': 'KPI'} | {'type': 'Property', 'value': {'ElecUse': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Total-Load', 'unit': 'KWH'}, 'ExtFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Air-Flow-Extraction', 'unit': 'MQH'}, 'SupFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Air-Flow-Supply', 'unit': 'MQH'}}} | {'type': 'Property', 'value': {'scope': {'type': 'enum', 'values': ['1 minute', '5 minutes', '15 minutes', 'hourly', 'daily', 'weekly', 'yearly']}}} | {'type': 'Property', 'value': 'A28-K:SC500-V01'} | {'type': 'Property', 'value': 'Specific Electricity Use'}
Task | urn:ngsi-ld:Task:KPI:Specific_Fan_Power | {'type': 'Property', 'value': 'KPI definition for the specific fan power in the AHU, takes as input a timeseries of fan power and fan flow outputs the sum specific fan power over the entire timeseries as a float'} | {'type': 'Property', 'value': 'KPI'} | {'type': 'Property', 'value': {'ExtFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Exhaust-Fan-Flow', 'unit': 'MQH'}, 'ExtFanPower': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Exhaust-Fan-Power', 'unit': 'KWT'}, 'SupFanFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Flow', 'unit': 'MQH'}, 'SupFanPower': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Power', 'unit': 'KWT'}}} | {'type': 'Property', 'value': {'scope': {'type': 'enum', 'values': ['1 minute', '5 minutes', '15 minutes', 'hourly', 'daily', 'weekly', 'yearly']}}} | {'type': 'Property', 'value': 'A28-K:SC500-V04'} | {'type': 'Property', 'value': 'Specific Fan Power'}
Task | urn:ngsi-ld:Task:KPI:Specific-Heating-Energy-Use | {'type': 'Property', 'value': 'KPI definition for the specific heating energy use for the AHU, takes as input a timeseries of supply air flow, extracion air flow, and electricity use to heat and outputs the specific electricity use over the entire timeseries as a float'} | {'type': 'Property', 'value': 'KPI'} | {'type': 'Property', 'value': {'HeatEnergyUse': {'type': 'Device', 'category': 'Sensor', 'controlsProperty': 'Energy-Consumed-Heating-Coil', 'unit': 'WHR'}, 'SupFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Air-Flow-Supply', 'unit': 'MQH'}}} | {'type': 'Property', 'value': {'scope': {'type': 'enum', 'values': ['1 minute', '5 minutes', '15 minutes', 'hourly', 'daily', 'weekly', 'yearly']}}} | {'type': 'Property', 'value': 'A28-K:SC500-V02'} | {'type': 'Property', 'value': 'Specific Heating Energy Use'}
Task | urn:ngsi-ld:Task:KPI:Water_Based_Heating_Energy_Use | {'type': 'Property', 'value': 'KPI definition for the specific heating energy use in the AHU, takes as input a timeseries of heating energy use and the flow rate over the heating coil and outputs the specific heating energy use over the entire timeseries as a float'} | {'type': 'Property', 'value': 'KPI'} | {'type': 'Property', 'value': {'ElecUse': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Energy-Consumed-Heating-Coil', 'unit': 'WHR'}, 'SupFlow': {'type': 'Device', 'category': 'Sensor', 'measuresProperty': 'Supply-Fan-Flow', 'unit': 'MQH'}}} | {'type': 'Property', 'value': {'scope': {'type': 'enum', 'values': ['1 minute', '5 minutes', '15 minutes', 'hourly', 'daily', 'weekly', 'yearly']}}} | {'type': 'Property', 'value': 'A28-K:SC500-V05'} | {'type': 'Property', 'value': 'Water Based Heating Energy Use'}